Fuel and Cladding

| Fuel | UO2 pellet |
| --- | --- |
| Cladding | Zr-4 |
| Enrichment | Initial: 2.1/2.6/3.1 % Reload: 3.2-4.0 % |
| Pellet Height | 12.9 mm |
| Pellet Diameter | 7.8 mm |
| Clad Thickness | 0.057 mm |
| Pin Height | 3850 mm |
| Pin Outside Diameter | 9.1 mm |
| Maximum Clad Temperature | 349 deg C |
| Maximum Centerline Temperature | 2593 deg C |

Fuel Assemblies

| Number of Rods per Assembly | 264 |
| --- | --- |
| Fuel Rod Pitch | 1.26 cm |
| Total Number of Assemblies | 193 |
| Fuel Assembly Pitch | 21.5 cm |
| Geometry | 17x17 |

Core Configuration

| Active Core Height | 3.65 m |
| --- | --- |
| Active Core Diameter | 3.37 m |
| Fuel Inventory | 101 tHM |
| Average Core Power Density | 104.5 kWt/liter |
| Peak Core Power Density | 232.0 kWt/liter |
| Average Assembly Discharge Burnup | 33000 MWd/tU |
| Average Linear Fuel Rating | 18.30 kW/m |

Control System

| Control Rod Material | Hf |
| --- | --- |
| Control Rod Drive Type | magnetic jack |
| Number of Coarse Control Rods | 25 |
| Number of Safety Rods | 28 |
| Number of Rods Containing Burnable Poison | 100 |
| Burnable Poison Material | borosilicate |
| Other Control Systems | chemical shim/burnable poison |

Primary Coolant

| Coolant Material | H2O |
| --- | --- |
| Pressure | 158 kg/sq cm |
| Core Inlet Temperature | 292 deg C |
| Core Outlet Temperature | 326 deg C |
| Number of Primary Pumps | 4 |
| Total Mass Flow | 15470 t/h |

Coolant Systems

| Number of Loops | 4 |
| --- | --- |
| Steam Generator Model/Series | D4 |
| Steam Generator Tube Material | Inconel 600 |
| Water Chemistry |  |

Turbines

| Number of Turbines | 1 |
| --- | --- |
| Turbine Speed | 1800 rev/min |
| Turbine Rating | 1175 MWe |
| Stop Valve Pressure | 67.6 kg/sq cm |
| Stop Valve Temperature | 282 deg C |

Vessel and Containment

| Vessel Material | SA 304 |
| --- | --- |
| Vessel Shape | cylinder |
| Height | 13.36 m |
| Inner Diameter | 4.39 m |
| Wall Thickness | 216 mm |
| Clad Thickness | 3.2 mm |
| Containment Type | reinforced concrete/steel |
| Containment Design Pressure | 4.3 kg/sq cm |

Reactor Operations

| Cycle Length | 18 months |
| --- | --- |
| Normal Planned Outage Length | 60-90 days |
| Fuel Loading | 29.2 tHM/y |
| Operational Strategy |  |

Spent Fuel Management

| Number of Operating Cycles Completed | 3 |
| --- | --- |